## Sheet1
| Serial Number | Sv2 Field Name | Enquiry Field Name (Customer Spec) | Enquiry Field Value (Customer Spec) | Units | Mapping Category | Field Requirement | Logic | Value for Sv2 Field | Service Dependency | Sector Dependency | Similar Field Terminologies | Similar Field Values | SV2 Spec Row Number | Sv2 Spec Field Name | Notes and Validations | Additional Information
0 | 1 | Tag No | Tag No. (Row 1) | 1803-FV-10401 ¦ 1803-FV-1104 ¦ 1803-FV- 1403 | — | Direct | Mandatory | Copy tag number verbatim from top of Enquiry DS (Row 1, left column) | 1803-FV-10401 ¦ 1803-FV-1104 ¦ 1803- FV-1403 | No | No | Tag Number; Instrument Tag; Tag ID; FV Tag | FV-XXXX; CV-XXXX; HCV-XXXX | Header | Tag No | Tag number must match the P&ID reference in Row 1. Format: Plant-Instrument-Number.
1 | 2 | Service | Service (Row 2) | SUSPECT CONDT PUMPS(P-606A/B) MCF ¦ LP STEAM TO E-101 PREHEATER ¦ RCSP HOPPER R-104 AERATION PLANT AIR | — | Direct | Mandatory | Copy service description verbatim from Row 2 of Enquiry DS | SUSPECT CONDT PUMPS(P-606A/B) MCF ¦ LP STEAM TO E-101 PREHEATER ¦ RCSP HOPPER R-104 AERATION PLANT AIR | No | No | Service Description; Valve Duty; Application | — | Row 1 | Service | May include equipment tag number in parentheses. Carry forward exactly as written.
2 | 3 | Fluid Name | Process Fluid (Row 14) | SUSPECT LP CONDENSATE ¦ LP Steam ¦ PLANT AIR | — | Direct | Mandatory | Copy fluid name from Row 14 of Enquiry DS | SUSPECT LP CONDENSATE ¦ Steam ¦ Air | Yes | No | Process Fluid; Fluid; Medium; Service Fluid | Water; Condensate; Steam; LP Steam; Plant Air; Nitrogen; Propylene | Row 2 | Fluid Name | Fluid name determines the sizing equation set (liquid, steam, or gas). Cross-check with Row 15 (Upstream Condition) for consistency.
3 | 4 | Fluid Phase | Upstream Condition (Row 15) | Water ¦ Steam ¦ Gas/Vapor | — | Derived | Mandatory | Map Row 15 value to Sv2 dropdown: Water/Liquid/Condensate → Liquid; Steam/LP Steam/HP Steam → Steam; Gas/Vapor/Air/Nitrogen → Gas | Liquid ¦ Steam ¦ Gas | Yes | No | State; Phase; Fluid State; Condition | Liquid; Vapour; Gas; Steam; Two- Phase | Row 3 | Fluid Phase | This selection determines the entire sizing equation path in Solutioneer. An incorrect phase will give a completely wrong Cv result.
4 | 5 | Inlet Pipe Size/Sch | Line Size and Schedule — Inlet (Row 11) | 3 in STD ¦ 12 in XS ¦ 6 in STD | in / Schedule | Direct | Mandatory | Extract inlet size and schedule from Row 11 Inlet column. Parse leading number as nominal size; schedule follows (STD, XS, 40S etc.) | 3 in/STD ¦ 12 in/XS ¦ 6 in/STD | No | No | Inlet Line Size; Upstream Line Size; Inlet Pipe Class; NPS | 1 in; 2 in; 3 in; 4 in; 6 in; 8 in; 12 in; STD; XS; SCH 40; SCH 80 | Row 4 | Inlet Pipe Size/Sch | Line size also embedded in Row 3 Line Number tag (e.g. '3"-CL-1803...' → 3 in). Use Row 11 as primary source.
5 | 6 | Outlet Pipe Size/Sch | Line Size and Schedule — Outlet (Row 11) | 3 in STD ¦ 12 in XS ¦ 6 in STD | in / Schedule | Direct | Mandatory | Extract outlet size and schedule from Row 11 Outlet column. Usually same as inlet unless expander is fitted. | 3 in/STD ¦ 12 in/XS ¦ 6 in/STD | No | No | Outlet Line Size; Downstream Pipe Size | Same as inlet in most cases | Row 5 | Outlet Pipe Size/Sch | If Outlet size differs from Inlet size, an expander/reducer is required. Flag for engineer review.
6 | 7 | Design Pressure (MAX) | Design Pressure / Temperature (Row 27) | 12 kgf/cm²-g ¦ 8 kgf/cm²-g ¦ 10 kgf/cm²-g | kgf/cm²-g | Direct | Mandatory | Extract maximum design pressure from Row 27 of Enquiry DS. This is the higher of the two values stated. | 12 kgf/cm²-g ¦ 8 kgf/cm²-g ¦ 10 kgf/cm²-g | No | No | Design Pressure; Max Design Pressure; DP MAX; MAWP | — | Row 6 | Design Temp(MAX/MIN) | Design pressure determines the ASME pressure class (150#, 300#, 600# etc.) per ASME B16.34 P- T tables.
7 | 8 | Design Pressure (MIN) | Design Pressure / Temperature (Row 27) | FV kgf/cm²-g ¦ FV kgf/cm²-g ¦ — (not stated) | kgf/cm²-g | Direct | Mandatory | Extract minimum design pressure from Row 27. FV = Full Vacuum = -1.033 kgf/cm²-a (or 0 absolute). Carry as 'FV' text if shown. | FV ¦ FV ¦ — | No | No | Min Design Pressure; Full Vacuum; FV; MDMP | FV; Full Vacuum; -1 barg; Vacuum | Row 7 | Design Pressure(MAX/MIN) | FV = Full Vacuum as design condition. See DS Page 2 process notes. Confirm with engineer before populating Sv2.
8 | 9 | Design Temp (MAX) | Design Pressure / Temperature (Row 27) | 150 °C ¦ 220 °C ¦ 65 °C | °C | Direct | Mandatory | Extract maximum design temperature from Row 27 of Enquiry DS. | 150 °C ¦ 220 °C ¦ 65 °C | No | No | Design Temperature; Max Temp; MADT; MDMT (max) | — | Row 7 | Design Temp(MAX/MIN) | Determines material grade selection (e.g. need for low-temp grades below -29°C, or high-temp grades above 230°C).
9 | 10 | Design Temp (MIN) / MDMT | Ambient Temperature (Row 5) / Process Notes Page 2 | 4.4 °C (MDMT from process notes all 3 tags) | °C | Derived | Mandatory | MDMT (Minimum Design Metal Temperature) stated in DS Page 2 Process Notes. Not the same as ambient temperature (Row 5). Extract from notes text. | 4.4 °C ¦ 4.4 °C ¦ 4.4 °C | No | No | MDMT; Min Design Metal Temperature; Low Temp; Cold Design Temp | — | Row 7 | Design Temp(MAX/MIN) | MDMT drives low-temperature material requirements (impact testing). Located in Page 2 Process Notes, not Row 5.
10 | 11 | Flow Rate (MAX) | Flow Rate @ Max Flow (Row 18) | 10.5 ¦ 6405 ¦ 2640 | Am³/h ¦ kg/h ¦ Nm³/h | Direct | Mandatory | Extract flow rate value from the '@ Max Flow' column of Row 18. Preserve units exactly as stated. | 10.5 m³/h ¦ 6405 kg/h ¦ 2640 Nm³/h | Yes | No | Maximum Flow Rate; Flow Max; Qmax; Mass Flow Max | m³/h; Am³/h; Nm³/h; kg/h; kg/s; lb/h | Row 11 | Flow rate | Units vary between liquid (Am³/h or kg/h) and gas (Nm³/h or kg/h). Check units column in Row 17 header row.
11 | 12 | Flow Rate (NOR) | Flow Rate @ Norm Flow (Row 18) | 9.5 ¦ 5823 ¦ 2400 | Am³/h ¦ kg/h ¦ Nm³/h | Direct | Mandatory | Extract flow rate value from the '@ Norm. Flow' column of Row 18. | 9.5 m³/h ¦ 5823 kg/h ¦ 2400 Nm³/h | Yes | No | Normal Flow Rate; Nominal Flow; Design Flow; Qnorm | Same as Max units | Row 11 | Flow rate | Normal (design) flow is the primary sizing case. Cv at Normal flow determines valve % travel target.
12 | 13 | Flow Rate (MIN) | Flow Rate @ Min Flow (Row 18) | 4.8 ¦ 2912 ¦ 2920 | Am³/h ¦ kg/h ¦ Nm³/h | Direct | Mandatory | Extract flow rate value from the '@ Min. Flow' column of Row 18. | 4.8 m³/h ¦ 2912 kg/h ¦ 2920 Nm³/h | Yes | No | Minimum Flow Rate; Qmin; Low Flow | Same as Max units | Row 11 | Flow rate | Minimum flow case checks that valve does not throttle too close to closed position (< 10% travel).
13 | 14 | Inlet Pressure (MAX) | Inlet Pressure @ Max Flow (Row 19) | 6.8 ¦ 3.31 ¦ 4.3 | kgf/cm²-g | Direct | Mandatory | Extract inlet pressure from '@ Max Flow' column of Row 19. | 6.8 kgf/cm²-g ¦ 3.31 kgf/cm²-g ¦ 4.3 kgf/cm²-g | No | No | P1 Max; Upstream Pressure Max; Inlet P Max | bar-g; kPa-g; psi-g; kgf/cm²-g; kgf/cm²-a | Row 12 | Inlet Press. | Check gauge vs absolute units. Enquiry DS uses kgf/cm²-g (gauge). If absolute ('a'), subtract 1.033 to convert to gauge.
14 | 15 | Inlet Pressure (NOR) | Inlet Pressure @ Norm Flow (Row 19) | 6.8 ¦ 3.31 ¦ 4.33 | kgf/cm²-g | Direct | Mandatory | Extract inlet pressure from '@ Norm. Flow' column of Row 19. | 6.8 kgf/cm²-g ¦ 3.31 kgf/cm²-g ¦ 4.33 kgf/cm²-g | No | No | P1 Norm; Upstream Pressure Normal; Inlet P Normal | Same as Max | Row 12 | Inlet Press.
15 | 16 | Inlet Pressure (MIN) | Inlet Pressure @ Min Flow (Row 19) | 6.9 ¦ 3.32 ¦ 4.4 | kgf/cm²-g | Direct | Mandatory | Extract inlet pressure from '@ Min. Flow' column of Row 19. | 6.9 kgf/cm²-g ¦ 3.32 kgf/cm²-g ¦ 4.4 kgf/cm²-g | No | No | P1 Min; Upstream Pressure Min | Same as Max | Row 12 | Inlet Press.
16 | 17 | Outlet Pressure (MAX) | Not directly stated — derived from Rows 19 & 20 | Calculated: 6.8 - 6.57 = 0.23 ¦ 3.31 - 0.3 = 3.01 ¦ 4.3 - 1.72 = 2.58 | kgf/cm²-g | Derived | Mandatory | Outlet Pressure = Inlet Pressure (Row 19) − Pressure Drop (Row 20) for each case. Sv2 requires explicit outlet pressure. | 0.23 kgf/cm²-g ¦ 3.01 kgf/cm²-g ¦ 2.58 kgf/cm²-g | No | No | P2 Max; Downstream Pressure Max; Back Pressure Max | — | Row 13 | Outlet Press. | If result is negative, check whether Enquiry DS uses absolute rather than gauge pressure. Flag for engineer confirmation.
17 | 18 | Outlet Pressure (NOR) | Not directly stated — derived from Rows 19 & 20 | Calculated: 6.8 - 6.6 = 0.20 ¦ 3.31 - 0.31 = 3.00 ¦ 4.33 - 1.74 = 2.59 | kgf/cm²-g | Derived | Mandatory | Outlet Pressure NOR = Inlet Press NOR (Row 19 NOR) − Pressure Drop NOR (Row 20 NOR) | 0.20 kgf/cm²-g ¦ 3.00 kgf/cm²-g ¦ 2.59 kgf/cm²-g | No | No | P2 Norm; Downstream Pressure Normal | — | Row 13 | Outlet Press.
18 | 19 | Outlet Pressure (MIN) | Not directly stated — derived from Rows 19 & 20 | Calculated: 6.9 - 6.7 = 0.20 ¦ 3.32 - 0.32 = 3.00 ¦ 4.4 - 1.83 = 2.57 | kgf/cm²-g | Derived | Mandatory | Outlet Pressure MIN = Inlet Press MIN (Row 19 MIN) − Pressure Drop MIN (Row 20 MIN) | 0.20 kgf/cm²-g ¦ 3.00 kgf/cm²-g ¦ 2.57 kgf/cm²-g | No | No | P2 Min; Downstream Pressure Min | — | Row 13 | Outlet Press.
19 | 20 | Pressure Drop (MAX) | Pressure Drop @ Max Flow (Row 20) | 6.57 ¦ 0.3 ¦ 1.72 | kgf/cm² | Direct | Mandatory | Extract pressure drop from '@ Max Flow' column of Row 20. | 6.57 kgf/cm² ¦ 0.3 kgf/cm² ¦ 1.72 kgf/cm² | No | No | dP Max; Delta P Max; Differential Pressure Max; ΔP | bar; kPa; psi; kgf/cm² | Row 14 | Pressure drop | Pressure drop at max flow gives the largest Cv but may not be the most critical case for control.
20 | 21 | Pressure Drop (NOR) | Pressure Drop @ Norm Flow (Row 20) | 6.6 ¦ 0.31 ¦ 1.74 | kgf/cm² | Direct | Mandatory | Extract pressure drop from '@ Norm. Flow' column of Row 20. | 6.6 kgf/cm² ¦ 0.31 kgf/cm² ¦ 1.74 kgf/cm² | No | No | dP Norm; Delta P Normal | Same as Max | Row 14 | Pressure drop
21 | 22 | Pressure Drop (MIN) | Pressure Drop @ Min Flow (Row 20) | 6.7 ¦ 0.32 ¦ 1.83 | kgf/cm² | Direct | Mandatory | Extract pressure drop from '@ Min. Flow' column of Row 20. | 6.7 kgf/cm² ¦ 0.32 kgf/cm² ¦ 1.83 kgf/cm² | No | No | dP Min; Delta P Min | Same as Max | Row 14 | Pressure drop
22 | 23 | Temperature (MAX) | Inlet Temperature @ Max Flow (Row 21) | 99.9 ¦ 160 ¦ 40 | °C | Direct | Mandatory | Extract temperature from '@ Max Flow' column of Row 21. | 99.9 °C ¦ 160 °C ¦ 40 °C | Yes | No | T Max; Process Temperature Max; Fluid Temp Max | °C; °F; K | Row 15 | Temperature | High temperature affects packing selection, bonnet type, and body material grade.
23 | 24 | Temperature (NOR) | Inlet Temperature @ Norm Flow (Row 21) | 99.9 ¦ 160 ¦ 40 | °C | Direct | Mandatory | Extract temperature from '@ Norm. Flow' column of Row 21. | 99.9 °C ¦ 160 °C ¦ 40 °C | Yes | No | T Norm; Process Temperature Normal | Same as Max | Row 15 | Temperature
24 | 25 | Temperature (MIN) | Inlet Temperature @ Min Flow (Row 21) | 99.99 ¦ 160 ¦ 40 | °C | Direct | Mandatory | Extract temperature from '@ Min. Flow' column of Row 21. | 99.99 °C ¦ 160 °C ¦ 40 °C | Yes | No | T Min; Process Temperature Min | Same as Max | Row 15 | Temperature
25 | 26 | Specific Gravity / Molecular Weight | Inlet Density / Specific Gravity / Molecular Mass (Row 22) | 955 kg/m³ (SG=0.955) ¦ — (steam) ¦ 28.96 (MW) | kg/m³ or dimensionl ess or g/mol | Derived | Mandatory | Liquid service: Row 22 gives density in kg/m³ → divide by 1000 to get SG (e.g. 955/1000 = 0.955). Gas service: Row 22 gives MW in g/mol (e.g. 28.96 for air). Steam service: leave blank; Sv2 uses steam | SG = 0.955 ¦ Blank (steam) ¦ MW = 28.96 g/mol | Yes | No | Spec. Gravity; SG; Specific Gravity; Molecular Weight; MW; Density; Relative Density | kg/m³; kg/L; g/cm³; dimensionless SG; g/mol | Row 17 | Spec. Gravity | Units must be verified. If Row 22 header says 'kg/m³' for a liquid, divide by 1000 for SG. If already dimensionless, use directly.
26 | 27 | Viscosity | Inlet Viscosity (Row 24) | 0.276 ¦ 0.014 ¦ 0.0191 | cP | Direct | Mandatory | tables. Copy viscosity value from Row 24 of Enquiry DS. | 0.276 cP ¦ 0.014 cP ¦ 0.0191 cP | Yes | No | Viscosity; Dynamic Viscosity; Kinematic Viscosity; μ; Centipoise | cP; mPa·s; cSt (note: cSt ≠ cP for density ≠ 1) | Row 18 | Viscosity | Viscosity affects Fp correction factor for high- viscosity liquids. If in cSt, convert: cP = cSt × SG.
27 | 28 | Compressibility Factor (Z) | Inlet Compressibility Factor (Row 23) | — (liquid; not applicable) ¦ — (steam) ¦ 0.999 | Dimensionl ess | Direct | Conditional | Extract Z from Row 23. Applicable for gas/vapour only. Leave blank for liquid and steam (Sv2 applies steam tables). | N/A (liquid) ¦ N/A (steam) ¦ 0.999 | Yes | No | Z Factor; Gas Compressibility; Compressibility; Z | 0.95 to 1.05 typical range | Row 16 | Z | For ideal gases Z = 1.0. If Row 23 is blank for a gas service, use Z = 1.0 as default.
28 | 29 | Specific Heats Ratio (K) | Inlet Specific Heats Ratio (Row 25) | — (liquid; not applicable) ¦ 1.317 (steam) ¦ 1.4 (air) | Dimensionl ess | Direct | Conditional | Extract K from Row 25. Applicable for gas and steam only. Leave blank for liquid services. | N/A (liquid) ¦ 1.317 ¦ 1.4 | Yes | No | Isentropic Exponent; Cp/Cv; Gamma; K; Specific Heat Ratio | Air = 1.4; Steam ≈ 1.3; Nitrogen = 1.4; CO2 = 1.3 | Row 18 | K | K affects the choked flow (critical pressure drop ratio) calculation. If not stated for a gas service, use 1.4 as conservative default for diatomic gases.
29 | 30 | Vapour Pressure | Inlet Vapour Pressure (Row 26) | 1.031 kgf/cm²-a ¦ — (steam; not applicable) ¦ — (gas; not applicable) | kgf/cm²-a | Direct | Conditional | Extract vapour pressure from Row 26. Applicable for liquid services only. Used to check cavitation and flashing. | 1.031 kgf/cm²-a ¦ N/A ¦ N/A | Yes | No | Pv; Vapour Pressure; Psat; Liquid Vapour Pressure | kgf/cm²-a; bar-a; psia; kPa-a | Row 16 | Vapour Press. | Must be in absolute pressure units. If given as gauge, add 1.033 kgf/cm² to convert to absolute.
30 | 31 | Valve Type | Body Type (Row 32) | Single Seat Globe ¦ Single Seat Globe ¦ Single Seat Globe | — | Direct | Mandatory | Copy body type from Row 32 of Enquiry DS verbatim. | Single Seat Globe ¦ Single Seat Globe ¦ Single Seat Globe | Yes | No | Body Type; Valve Type; Valve Body Style; Body Style | Single Seated Globe; Double Seated Globe; Butterfly; Ball; Angle; Y-Pattern | Row 27 | Type | Valve type is always stated by the customer in this format. Do not leave for engineer to determine.
31 | 32 | Body Material | Body Material (Row 36) | F.S. ASTM A105 Normalized ¦ C.S. ASTM A216 WCB ¦ C.S. ASTM A216 WCB | — | Direct | Mandatory | Copy body material specification verbatim from Row 36 of Enquiry DS. This is fully stated by the customer. | F.S. ASTM A105 Normalized ¦ ASTM A216 Gr. WCC ¦ ASTM A216 Gr. WCC | Yes | Yes | Body Material; Body MOC; Body Grade; Pressure Boundary Material | A105; A216 WCB; A216 WCC; A351 CF8M; A351 CF3M; A182 F316 | Row 29 | Body Material | Note: Enquiry DS says 'A216 WCB' while KSB MIL DS shows 'A216 Gr. WCC' — verify with engineer. WCB and WCC are different grades. Do not silently change.
32 | 33 | Bonnet Type | Bonnet Type / Material (Row 37) | Bolted Flange A105 ¦ Bolted Flange A216 WCB ¦ Bolted Flange A216 WCB | — | Direct | Mandatory | Copy bonnet type and material from Row 37 of Enquiry DS. | Bolted Flange A105 ¦ Bolted Flange A216 WCB ¦ Bolted Flange A216 WCB | Yes | No | Bonnet Type; Bonnet; Bonnet Style; Bonnet Material | Standard; Extended; Finned Extension; Cryogenic; Bolted Flange; Pressure Seal | Row 35 | Bonnet Type | Extended or finned bonnet required for steam above 200°C or cryogenic services. Check pipe insulation (Row 13) for guidance.
33 | 34 | Flow Direction | Flow Direction (Row 38) | FTC (Flow-To-Close) ¦ FTO (Flow-To-Open) ¦ FTO (Flow-To-Open) | — | Direct | Mandatory | Copy flow direction from Row 38 of Enquiry DS. FTC = Flow-To-Close; FTO = Flow-To-Open. | Flow to close ¦ Flow to open ¦ Flow to open | Yes | No | Flow Direction; FTC; FTO; Flow-To- Close; Flow-To-Open; Flow Under Seat | FTC; FTO; Over the seat; Under the seat | Row 31 | Flow Direction | Flow direction affects actuator unbalance forces and determines stability. Customer-specified; do not change.
34 | 35 | End Connection & Rating | End Connec. & Rating (Row 35) | 1.5" 300# RF ¦ 8" 300# RF ¦ 4" 300# RF | — | Direct | Mandatory | Copy end connection type, size, and rating from Row 35 of Enquiry DS. | Flanged-ASME 300 RF ¦ Flanged-ASME 300 RF ¦ Flanged-ASME 300 RF | No | No | End Connection; Flange Rating; ANSI Class; Flange Type; Body Rating | ASME 150 RF; ASME 300 RF; ASME 600 RF; ASME 900 RTJ; Butt Weld | Rows 30/32/33 | End Conn. (Inlet/Outlet) | Body size shown in Row 33 ('By Vendor') means KSB MIL selects from catalogue after Cv calculation. Rating determines the body design pressure.
35 | 36 | Flow Characteristic | Characteristic (Rated Cv / Characteristic Row 34) | Linear ¦ Equal% ¦ Linear | — | Derived | Mandatory | Row 34 shows 'By Vendor ¦ Equal% ¦ By Vendor'. For 'By Vendor', engineer selects based on process control requirements: Equal Percentage for pressure- drop ratio > 0.3; Linear for most other cases. | Linear ¦ Equal % ¦ Linear | Yes | No | Characteristic; Flow Characteristic; Inherent Characteristic; Cv Characteristic | Linear; Equal Percentage; Quick Opening; Modified Parabolic | Row 40 | Characteristic | Equal Percentage selected when the valve pressure drop varies significantly across the flow range. Linear when pressure drop is relatively constant.
36 | 37 | Trim / Plug Type | Trim Type (Row 42) | Low Noise Trim ¦ Contoured Trim ¦ Low Noise Trim | — | Direct | Mandatory | Copy trim type from Row 42 of Enquiry DS verbatim. | Low Noise Trim (Anti-Cavitation) ¦ Contoured Trim ¦ Low Noise Trim | Yes | No | Trim Type; Plug Type; Trim Style; Plug Style; Cage Type | Standard Contoured; Low Noise; Anti-Cavitation; Parabolic; V-Port; Characterized | Row 42 | Plug Type | Low Noise trim is specified because SPL at max flow approaches or exceeds allowable. Verify SPL result after Cv calculation.
37 | 38 | Plug Material | Plug / Ball / Disk Material (Row 44) | 410 (13Cr) ¦ 410 (13Cr) ¦ 410 (13Cr) | — | Direct | Mandatory | Copy plug material from Row 44 of Enquiry DS verbatim. | SS 410 + Stellite No.6 ¦ SS 410 + Stellite No.6 ¦ SS 410 + Stellite No.6 | Yes | Yes | Plug Material; Ball Material; Disk Material; Trim Material; Plug MOC | SS 316; SS 410; 17-4PH; Stellite overlay; Hastelloy C | Row 46 | Plug Material | Enquiry DS states '410 (13Cr)'; KSB MIL DS output shows 'SS 410 + Stellite No.6' — the Stellite hard-facing is a KSB MIL standard addition for corrosion and erosion resistance.
38 | 39 | Seat Material | Seat Material (Row 45) | St Gr6 (CoCrAlloy) ¦ St Gr6 (CoCrAlloy) ¦ St Gr6 (CoCrAlloy) | — | Direct | Mandatory | Copy seat material from Row 45 of Enquiry DS verbatim. | SS 410 + Stellite No.6 ¦ SS 410 + Stellite No.6 ¦ SS 410 + Stellite No.6 | Yes | Yes | Seat Material; Seat Ring Material; Seat MOC | SS 316; SS 410; Stellite; Monel; Inconel | Row 47 | Seat Material | 'St Gr6' = Stellite Grade 6 (Cobalt-Chromium alloy). KSB MIL DS shows seat as SS 410 + Stellite overlay. Confirm mapping with engineer.
39 | 40 | Seat Leakage Class | Tightness Requirements (Row 7) | ANSI IV (standard) ¦ ANSI IV (standard) ¦ ANSI V | — | Derived | Mandatory | Map customer tightness requirement to FCI 70.2 leakage class: ANSI IV → IV (FCI 70.2); ANSI V → V (FCI 70.2); ANSI VI → VI (FCI 70.2) | IV (FCI 70.2) ¦ IV (FCI 70.2) ¦ V (FCI 70.2) | No | No | Leakage Class; Seat Leakage; Tightness Class; Shut-off Class | Class I; Class II; Class III; Class IV; Class V; Class VI; Zero Leakage | Row 41 | Seat Leakage Class | Class V required for Tag 3 (ANSI V). Class V requires lapped metal seat. Increases cost and lead time. Flag for review.
40 | 41 | Guiding | Guiding / No. of Ports (Row 41) | By Vendor / 1 (all tags) | — | Engineered | Optional | 'By Vendor' means KSB MIL selects guiding arrangement. Standard for single-seated globe: Heavy Top Guiding for Tag 1 and 3; Cage Guiding for Tag 2 (heavy-duty steam). | Heavy Top Guiding ¦ Cage Guiding ¦ Heavy Top Guiding | Yes | No | Guiding; Guide Type; Plug Guiding; Top-and-Bottom Guiding | Top Guided; Cage Guided; Top- and-Bottom Guided; Port Guided | Row 45 | Guiding | Guiding selection affects valve stability at high pressure drops. KSB MIL selects based on valve series and dP ratio.
41 | 42 | Actuator Type | Type (Actuator) (Row 50) | Spring Diaphragm ¦ Spring Diaphragm ¦ Spring Diaphragm | — | Direct | Mandatory | Copy actuator type from Row 50 of Enquiry DS. | Pneumatic Spring Diaphragm ¦ Pneumatic Spring Diaphragm ¦ Pneumatic Spring Diaphragm | No | No | Actuator Type; Actuator Style; Pneumatic Actuator; Diaphragm Actuator | Spring Diaphragm; Piston; Scotch- Yoke; Electric; Electro-Hydraulic | Row 51 | Type | All three tags use Spring Diaphragm type — the most common pneumatic actuator. Piston actuator used for high shut-off or large bore valves.
42 | 43 | Actuator Action / Air Failure | Power Failure Position (Row 9) + Air Failure Valve (Row 52) | Open (R9) / Open (R52) ¦ Close (R9) / Close (R52) ¦ Open (R9) / Open (R52) | — | Derived | Mandatory | Row 9 = Power Failure Position (safe position on air loss). Map: Fail Open → Air to Close (ATC); Fail Close → Air to Open (ATO). Row 52 confirms. Cross- check both rows. | Air to Close (ATC) ¦ Air to Open (ATO) ¦ Air to Close (ATC) | Yes | No | Fail Position; Fail Safe; Air Failure; FO; FC; Air to Close; Air to Open; ATC; ATO | FO (Fail Open); FC (Fail Close); FL (Fail Last); Air to Close; Air to Open | Rows 53/54 | Action / Air Failure | Actuator colour coding follows: ATC (Fail Open) → GREEN actuator; ATO (Fail Close) → RED actuator. See KSB MIL DS Sheet 2 Row 112.
43 | 44 | Supply Pressure | Available Air Supply Pressure (Row 8) | Min 3.5 kgf/cm² / Max 7 kgf/cm² (all tags) | kgf/cm² | Derived | Mandatory | Use minimum available supply pressure from Row 8. Convert to psi: × 14.223. Round to nearest standard value. 3.5 kgf/cm² × 14.223 ≈ 50 psi. | 50 psi (all tags) | No | No | Air Supply; Instrument Air; IA Supply; Air Supply Pressure; Pneumatic Supply | 35 psi; 50 psi; 60 psi; 80 psi | Row 56 | Supply Press. | Use minimum supply to ensure actuator can stroke even at lowest supply condition. Bench range must be set below supply pressure minus positioner overhead (~5 psi).
44 | 45 | Bench Range | Bench Range (Row 54) | By Vendor ¦ By Vendor ¦ By Vendor | psi | Engineered | Mandatory | 'By Vendor' on all three tags → KSB MIL calculates bench range from actuator sizing (spring rate × travel + preload). Typical values: 3-15 psi, 6-30 psi. KSB MIL DS shows 3-15 psi (Tag1) and 6-30 psi | 3-15 psi (Tag1) ¦ 6-30 psi (Tag2) ¦ 5-18 psi (Tag3) | No | No | Bench Range; Spring Range; Spring Calibration; Air Range; Bench Set | 3-15 psi; 6-30 psi; 3-27 psi; 6-18 psi | Row 55 | Bench Range | Bench range calculated by actuator sizing to ensure adequate shut-off thrust. Cannot be determined from Enquiry DS alone — leave for engineer.
45 | 46 | Shut-off Pressure | Actuator Design Pressure (Row 10) | Not stated in Enquiry DS — derived from Row 27 Design Pressure | kgf/cm² | Derived | Mandatory | (Tag2). Shut-off pressure = maximum design pressure of valve (Row 27 MAX). KSB MIL DS Row 57 shows this value. | 12 kgf/cm² (Tag1) ¦ 8 kgf/cm² (Tag2) ¦ 10 kgf/cm² (Tag3) | No | No | Shut-off Pressure; Actuator Rating; MAOP; Max Operating Pressure; Differential Shut-off Pressure | — | Row 57 | Shut off Press. | Used to size actuator spring and diaphragm area to ensure valve closes tightly against max design pressure.
46 | 47 | Handwheel | Handwheel (Row 53) | — (dash; not specified) ¦ — (dash) ¦ Side Mounted | — | Direct | Optional | Copy handwheel requirement from Row 53. '—' or blank = No handwheel. 'Side Mounted' = side- mounted handwheel assembly. | No/NA ¦ No/NA ¦ Yes/6A2 (Side Mounted) | No | No | Handwheel; Manual Override; Manual Operator; Side Handwheel; Top Handwheel | No; NA; Side Mounted; Top Mounted; Integral | Row 58 | Hand Wheel/Model | Tag 3 (Plant Air) requires side-mounted handwheel. This is a manual override device — allows operator to position valve when air supply is unavailable.
47 | 48 | Positioner Type | Not stated in Enquiry DS (Row 56 = VTA/VTA) | VTA / VTA (all tags) | — | Engineered | Mandatory | VTA = Vendor To Advise. KSB MIL selects standard smart positioner: Smart Single Acting (HART). Selection standard for all modulating control valves. | Smart Single Acting | No | No | Positioner Type; Positioner Style; Electro-Pneumatic Positioner | Single Acting; Double Acting; Smart; Conventional; Digital | Row 72 | Type | Smart positioner integrates position transmitter — eliminates need for separate position transmitter hardware.
48 | 49 | Positioner Make | Positioner MFR (Row 56) | VTA (all tags) | — | Derived | Mandatory | VTA → KSB MIL standard selection: METSO. If customer specifies a make (not VTA), copy directly. | METSO | No | No | Positioner Manufacturer; Positioner Make; Brand | METSO; SAMSON; FISHER; ABB; SIEMENS; ROTORK | Row 73 | Make | METSO ND9103 is the KSB MIL standard positioner. Alternative approved make: SAMSON 3730.
49 | 50 | Positioner Model | Positioner Model (Row 56) | VTA (all tags) | — | Derived | Mandatory | VTA → KSB MIL standard model: ND9103-HX-T (HART communication, aluminium housing, ATEX certified). | ND9103-HX-T | No | No | Positioner Model; Model Number | ND9103-HX-T; TZID-C; 3731-3; DVC6200 | Row 74 | Model | ND9103-HX-T: HX = HART with XP rating; T = with position transmitter integrated.
50 | 51 | Positioner Protocol / Casing | Signal Inlet (Row 57) | 4-20mA+HART / 3-15Psi (all tags) | — | Derived | Mandatory | Signal '4-20mA+HART' → Protocol = HART. Standard casing = Aluminium (IP66). Combined field: HART/Aluminium. | HART/Aluminium | No | No | Communication Protocol; Positioner Protocol; Housing Material; Casing | HART; FOUNDATION Fieldbus; PROFIBUS PA; 4-20mA only | Row 75 | Protocol / casing
51 | 52 | Positioner Action / Input Signal | Signal Inlet (Row 57) + Increase Signal Valve (Row 58) | 4-20mA+HART, Increase Signal = Close (Tags 1&3) / Open (Tag 2) | mA | Derived | Mandatory | Combine action sense and signal: 'Increase Signal → Close' = Direct Acting. 'Increase Signal → Open' = Reverse Acting. All tags use 4-20 mA input. Result: 'Direct/4-20 mA' for ATC valves. | Direct/4-20 mA (all tags) | Yes | No | Action; Input Signal; Positioner Action; Direct Acting; Reverse Acting | Direct/4-20mA; Reverse/4-20mA; Direct/3-15psi; Split-range | Row 76 | Action/Input Signal | 'Increase Signal → Close' means as signal increases, valve closes. This is Direct Acting positioner (increasing air closes valve = ATC). For ATO valves, Increase Signal → Open is
52 | 53 | Positioner Certification | Area Classification (Row 4) | Zone 1 Gr. IIC T3 (all tags) | — | Derived | Mandatory | Zone 1 IIC T3 → Intrinsic Safety certification required: 'Intrinsic Safe Ex ia IIC, T6, with Weather Proof IP 66 Enclosure' | Intrinsic Safe Ex ia IIC, T6, WP IP66 | No | Yes | ATEX Certification; Hazardous Area Certificate; Ex Certification; IS Certificate | Ex ia; Ex d; EEx e; Ex n; PESO Certificate | Row 77 | Certification | typical. Zone 1 requires Intrinsic Safety (Ex ia) or Flameproof (Ex d) certification. KSB MIL standard uses Ex ia for positioner. PESO certificate also required (see quality requirements).
53 | 54 | Position Transmitter | Position Transmitter (Row 61) | Yes. 4-20mA+Hart (all tags) | — | Derived | Conditional | 'Yes' → Position transmitter is integral to the smart positioner (METSO ND9103). No separate device. Mounting: Integral to Smart Positioner. Output: 24 VDC / 4-20 mA (voltage from Row 62). | Integral to Smart Positioner / 24 VDC / 4- 20mA | No | No | Position Transmitter; Stem Position Transmitter; Position Feedback; LVDT | Integral; Separate; Remote Mount; LVDT; Hall Effect | Rows 86–89 | Type / Make/Model / Supply/Output | If Row 61 = 'No', populate Rows 86–92 as 'Not Required'. If a separate transmitter is specified (non-integral), treat as Engineered selection.
54 | 55 | Airset Make/Model/Qty | Air Set MFR / Model (Row 72) | VTA / VTA / VTA (all tags) | — | Derived | Mandatory | VTA → KSB MIL standard: Shavo SB77-276-M6KN- N, 1 No. Gauges: Yes (Row 74) → include pressure gauge. | Shavo/SB77-276-M6KN-N/1 No | No | No | Air Set; Filter Regulator; AFR; Airset; Filter Reg Unit | Shavo; Norgren; SMC; Parker; Watts | Row 67 | Make/Model/Qty | Airset conditions instrument air (filters and regulates) before it enters positioner and actuator. Filter: 5 micron standard.
55 | 56 | Airset Set Pressure / Filter | Airset Set Pressure (Row 73) / Filter (Row 74) | By Vendor / Gauge: Yes (all tags) | — | Derived | Mandatory | Set pressure = minimum available air supply (Row 8 MIN) = 3.5 kgf/cm² ≈ 50 psi. Filter size: standard = 5 micron. Gauge: Yes. | Set Pressure: By Vendor / Filter: 5 Micron / Gauge: Yes | No | No | Set Pressure; Filter Size; Micron Rating; Filter Element | 5 micron; 25 micron; 40 micron; 0.3 micron | Rows 68/73/74 | Filter Size / Set Press / Gauge
56 | 57 | Painting Scheme | Not in standard Enquiry DS body — from PO/project | Not stated in Enquiry DS | — | Engineered | Mandatory | KSB MIL standard: Body — SPECIAL ¦ Actuator — SPECIAL. Painting procedure reference from project PO (e.g. CP 121_PK233545). | Body - SPECIAL ¦ Actuator - SPECIAL | No | Yes | Painting; Paint Scheme; Surface Treatment; Colour Code | RAL 7001; IT 228HS; Epoxy; Primer + Top coat | Row 111 | Painting Scheme | Painting scheme varies by project. Always refer to PO painting specification. Body colour: Grey (IT 228HS). Actuator colour: GREEN (fail-open) or RED (fail-close).
57 | 58 | Actuator Colour | Power Failure Position (Row 9) | Open ¦ Close ¦ Open | — | Derived | Mandatory | Fail Open (Row 9 = Open) → Actuator colour GREEN. Fail Close (Row 9 = Close) → Actuator colour RED. Body always GREY (IT 228HS). | GREEN ¦ RED ¦ GREEN | No | No | Actuator Colour; Actuator Color; Body Colour; Colour Code | Green; Red; Yellow; Grey | Row 112 | Body Colour / Actuator Colour | Colour coding is a visual safety indicator of fail- safe position. Standard: Green = Fail Open; Red = Fail Close.
58 | 59 | Cable Gland Type | Not in Enquiry DS | Not stated | — | Engineered | Mandatory | KSB MIL standard: Double compression type. Certification derived from Area Classification (Row 4). | Double compression type | No | No | Cable Gland; Gland Type; Cable Entry Device | Single compression; Double compression; Stopping plug; EMC gland | Row 130 | Type
59 | 60 | Cable Gland Certification | Area Classification (Row 4) | Zone 1 Gr. IIC T3 (all tags) | — | Derived | Mandatory | Zone 1 IIC → Explosion Proof: Ex d IIA, IIB, IIC. Material: SS 304 + PVC Hood. Cable Type: Flexible. | Explosion Proof Ex d IIA, IIB, IIC | No | Yes | Cable Gland Certification; Gland Cert; Hazardous Area Gland; ATEX Gland | Ex d; Ex e; Ex n | Row 131 | Certification | Cable gland certification must be independent of positioner certification. Even if positioner is Ex ia, cable gland must be rated Ex d for Zone 1.
60 | 61 | IBR Applicability | Process Fluid (Row 14/15) + Specification Notes (DS Page 2) | Not steam (Tag1/3); IBR Applicable (Tag2 — process notes state 'IBR Applicable') | — | Derived | Mandatory | If fluid = steam AND 'IBR' appears in DS Page 2 Spec/Process Notes → IBR applies. Valve must be tested and certified by IBR per Appendix L. Otherwise 'IBR Not Required'. | IBR Not Required (Tag1/3) ¦ IBR Certificate in Form IIIC (Tag2) | Yes | Yes | IBR; Indian Boiler Regulation; Boiler Certificate; IBR Certificate | IBR Applicable; IBR Required; Form IIIC; Not applicable to IBR | Rows 137/145 | Special Testing/Quality Requirements | IBR certificate requires third-party inspection during manufacturing. Increases lead time by 4-6 weeks. Flag immediately when identified.
61 | 62 | NDT — RT Extent | Not in Enquiry DS directly — standard requirement | Standard for all castings (Body, Bonnet, Flanges) | — | Derived | Mandatory | Standard KSB MIL requirement for all projects: 10% RT per lot for Body/Bonnet/Com.Flange/Expander/LNP. Trigger: always apply unless customer explicitly waives. | [0510] RT extent 10% per lot — BODY/BONNET/COM.FLANGE/EXP/LN P | No | No | RT; Radiographic Testing; X-Ray; NDE; NDT | 10% RT; 100% RT; Spot RT; UT (Ultrasonic) | Row 138 | Special Testing/Quality Requirements
62 | 63 | NDT — PMI Test | Not in Enquiry DS directly — standard requirement | Standard for all trim parts | — | Derived | Mandatory | Standard KSB MIL requirement: PMI Test (Standard grade) for all trim parts. Trigger: always apply. | [1801] PMI Test (Std) applicable for TRIM PARTS | No | No | PMI; Positive Material Identification; Material Test; XRF; Chemical Analysis | PMI Standard; PMI Full; 100% PMI; PMI on castings | Row 142 | Special Testing/Quality Requirements | PMI verifies that trim materials match specification (e.g. confirms SS 410 is not SS 304 supplied in error).
63 | 64 | NDT — IGC Test | Trim/Seat Material (Rows 44/45) — triggered by Austenitic SS | Plug: 410 (13Cr) — not austenitic, trigger NOT activated for these tags | — | Derived | Conditional | IGC test triggered when plug/seat material contains Austenitic Stainless Steel (SS316, CF8M, CF3M, 304 etc.). SS 410 (martensitic) and Stellite do NOT trigger IGC. For these three tags: IGC row is | [1707] IGC testing as per Prac.E, 250× microstructure (applicable for Aust.SS Trim Parts) | Yes | No | IGC; Intergranular Corrosion; Sensitisation Test; ASTM A262 Prac E | IGC Test; Weld Decay Test; Sensitisation | Row 139 | Special Testing/Quality Requirements | If trim material is changed to SS316 or CF8M in a future revision, IGC test becomes mandatory.
64 | 65 | Valve Operating Signature | Not in Enquiry DS — standard requirement | Standard for all control valves | — | Derived | Mandatory | populated as standard but may not be strictly Standard KSB MIL requirement: valve operating signature (stem position vs control signal) to be supplied on CD/soft copy. | [2805] Valves operating signature in the form of CD | No | No | Operating Signature; Valve Signature; Stroke Test Record; Loop Test | CD; PDF; Digital Report; FAT Record | Row 143 | Special Testing/Quality Requirements
65 | 66 | PESO Certificate | Area Classification (Row 4) | Zone 1 Gr. IIC T3 (all tags) | — | Derived | Mandatory | Hazardous area (Zone 1 or Zone 2) → PESO certificate required for all electrical accessories (positioner, solenoid valve if any, limit switches if any). | [2301] PESO Certificate for All Electrical Accessories | No | Yes | PESO; CCOE; Hazardous Area Certificate; Electrical Accessory Certificate | PESO; CCOE; Statutory approval | Row 144 | Special Testing/Quality Requirements | PESO (Petroleum and Explosives Safety Organisation) is the Indian statutory body. Certificate must be obtained before despatch. Add 4-6 weeks to delivery if not pre-certified.